## Sheet1
PROJECT NAME: | [Input Project Name] |  | Column2 | Column3 | Column4
UNIT TAG: | [Input Unit Tag]
DESIGN AIRFLOW: | [Input Design Airflow]
DATE: | [Input Date]
EXTERNAL STATIC PRESSURE CALCULATION | Standard Reference: SMACNA / ASHRAE
|  | Please FILL the QTY / LENGTH | Please FILL the PRESSURE DROP
DESCRIPTION | UNIT | QTY / LENGTH | PRESSURE DROP/UNIT | TOTAL (Pa) | REMARKS
A. SUPPLY AIR SIDE
Straight Ducting (Supply) | m | 30 | 1 | 30 | Friction Loss | DO NOT FILL THIS COLOURED CELL ⚠️ CONTAINS FORMULA
Elbow 90 Deg (Rectangular) | pcs | 4 | 6 | 24 | Fitting Loss | USER INPUT REQUIRED
Tee / Branch Fitting | pcs | 2 | 5 | 10 | Fitting Loss | USER INPUT REQUIRED
Reducer / Enlarger | pcs | 2 | 3 | 6 | Fitting Loss
Volume Control Damper (VCD) | pcs | 1 | 20 | 20 | Main Branch
Fire Damper (FD/MD) | pcs | 1 | 30 | 30 | Safety
Supply Diffuser / Grille | pcs | 1 | 25 | 25 | Terminal
Flexible Duct Connection | m | 1.5 | 3 | 4.5
SUB-TOTAL SUPPLY |  |  |  | 149.5
B. RETURN AIR SIDE
Straight Ducting (Return) | m | 10 | 1 | 10
Return Air Grille (RAG) | pcs | 1 | 20 | 20
Sound Attenuator | set | 0 | 50 | 0 | Optional
SUB-TOTAL RETURN |  |  |  | 30
C. FILTRATION SYSTEM
Pre-Filter (G4) | set | 1 | 50 | 50 | Initial PD
Medium Filter (F7/F8) | set | 0 | 100 | 0 | Initial PD
HEPA Filter (H13) | set | 0 | 300 | 0 | Final PD
SUB-TOTAL FILTERS |  |  |  | 50
CALCULATION SUMMARY
TOTAL SYSTEM RESISTANCE |  |  |  | 229.5 | Pa
SAFETY FACTOR (10%) |  |  |  | 22.95 | Pa
REQUIRED FAN ESP (Pascal) |  |  |  | 252.45 | Pa
REQUIRED FAN ESP (in. wg) |  |  |  | 1.0136 | in. wg
Provided by: https://engpocket.com/en/external-static-pressure-calculation-excel/